## Activity
Activity Code (Should be unique for each Activity) | Form Name | Activity Name | Activity Type | Service Type | Asset Codes (Separated by ¦ [pipe]) | Frequency | Assigned Days | Day Of Month | Quarter | HalfYear | Year | Start Date (Date the task should be scheduled from) | Start Time | End Time | Task Duration (In Minutes) | Group Name
ACT-002 | LT Energy Meter Reading | LT Energy Meter Reading | JobCard | TECHSERVICES | TRDB000059¦TRDB000060¦TRDB000061¦TRDB000062¦TRDB000063¦TRDB000064¦TRDB000065¦TRDB000066¦TRDB000067¦TRDB000068¦TRDB000069¦TRDB000070¦TRDB000071¦TRDB000072¦TRDB000073¦TRDB000074¦TRDB000075¦TRDB000076¦TRDB000077¦TRDB000078¦TRDB000079¦TRDB000080¦TRDB000081¦TRDB000082¦TRDB000083¦TRDB000084¦TRDB000085¦TRDB000086¦TRDB000087¦TRDB000088¦TRDB000089¦TRDB000090¦TRDB000091¦TRDB000092¦TRDB000093¦TRDB000094¦TRDB000095¦TRDB000096¦TRDB000097¦TRDB000098¦TRDB000099¦TRDB000100¦TRDB000101¦TRDB000102¦TRDB000103¦TRDB000104¦TRDB000105¦TRDB000106¦TRDB000107¦TRDB000108¦TRDB000109¦TRDB000110¦TRDB000111¦TRDB000112¦TRDB000113¦TRDB000114¦TRDB000115¦TRDB000116¦TRDB000117¦TRDB000118¦TRDB000119¦TRDB000120¦TRDB000121¦TRDB000122¦TRDB000123¦TRDB000124¦TRDB000125¦TRDB000126¦TRDB000127¦TRDB000128¦TRDB000129¦TRDB000130¦TRDB000131¦TRDB000132¦TRDB000133¦TRDB000134¦TRDB000135¦TRDB000136¦TRDB000137¦TRDB000138¦TRDB000139¦TRDB000140¦TRDB000141¦TRDB000142¦TRDB000143¦TRDB000144¦TRDB000145¦TRDB000146¦TRDB000147¦TRDB000148¦TRDB000149¦TRDB000150¦TRDB000151¦TRDB000152¦TRDB000153¦TRDB000154¦TRDB000155¦TRDB000177¦TRDB000178¦TRDB000179¦TRDB000180¦TRDB000181¦TRDB000182¦TRDB000183¦TRDB000184¦TRDB000185¦TRDB000186¦TRDB000187¦TRDB000188¦TRDB000189¦TRDB000190¦TRDB000191¦TRDB000192¦TRDB000193¦TRDB000194¦TRDB000195¦TRDB000196¦TRDB000197 | every1hour | [5 empty] | 2024-01-10 | 00:00:00 | 23:59:59 | 1440 | Electrician
ACT-003 | HT Panel Daily Checklist | HT Panel Daily Checklist | JobCard | TECHSERVICES | TRDB000885¦TRDB000887 | onceinaday | [5 empty] | 2024-01-10 | 00:00:00 | 23:59:59 | 1440 | Electrician
ACT-004 | Transformer Daily Checklist | Transformer Daily Checklist | JobCard | TECHSERVICES | TRDB000888¦TRDB000889¦TRDB000890¦TRDB000891 | onceinaday | [5 empty] | 2024-01-10 | 00:00:00 | 23:59:59 | 1440 | Electrician
ACT-005 | Panel Weekly PM Checklist | Panel Weekly PM Checklist | Planned | TECHSERVICES | TRDB000005¦TRDB000006¦TRDB000007¦TRDB000008¦TRDB000009¦TRDB000010¦TRDB000534¦TRDB000749¦TRDB000882¦TRDB000902¦TRDB000903¦TRDB000904¦TRDB000905¦TRDB000908¦TRDB000909¦TRDB000910¦TRDB000911¦TRDB000912¦TRDB000913¦TRDB000914¦TRDB000915¦TRDB001187¦TRDB001188¦TRDB001189¦TRDB001190¦TRDB001191¦TRDB001192¦ | onceinaday | 7 |  |  |  |  | 2024-01-10 | 00:00:00 | 23:59:59 | 2880 | Electrician
ACT-006 | AC Chiller Weekly PM Checklist | AC Chiller Weekly PM Checklist | Planned | TECHSERVICES | TRDB000931¦TRDB000932¦TRDB000933¦TRDB000934 | onceinaday | 7 |  |  |  |  | 2024-01-10 | 00:00:00 | 23:59:59 | 2880 | HVAC Technician
ACT-007 | WC Chiller Weekly PM Checklist | WC Chiller Weekly PM Checklist | Planned | TECHSERVICES |  | onceinaday | 7 |  |  |  |  | 2024-01-10 | 00:00:00 | 23:59:59 | 2880 | HVAC Technician
ACT-008 | Cooling Tower Weekly PM Checklist | Cooling Tower Weekly PM Checklist | Planned | TECHSERVICES |  | onceinaday | 7 |  |  |  |  | 2024-01-10 | 00:00:00 | 23:59:59 | 2880 | HVAC Technician
ACT-009 | Elevator Weekly PM Checklist | Elevator Weekly PM Checklist | Planned | TECHSERVICES | TRDB000516¦TRDB000517¦TRDB000518¦TRDB000519¦TRDB000520¦TRDB000521¦TRDB000522¦TRDB000523¦TRDB000524¦TRDB000525 | onceinaday | 7 |  |  |  |  | 2024-01-10 | 00:00:00 | 23:59:59 | 2880 | Electrician
ACT-010 | Cooling Tower Daily Checklist | Cooling Tower Daily Checklist | JobCard | TECHSERVICES |  | onceinaday | [5 empty] | 2024-01-10 | 00:00:00 | 23:59:59 | 1440 | HVAC Technician
ACT-012 | Elevator Daily Checklist | Elevator Daily Checklist | JobCard | TECHSERVICES | TRDB000516¦TRDB000517¦TRDB000518¦TRDB000519¦TRDB000520¦TRDB000521¦TRDB000522¦TRDB000523¦TRDB000524¦TRDB000525 | onceinaday | [5 empty] | 2024-01-10 | 00:00:00 | 23:59:59 | 1440 | Electrician

## Form Parameter
Activity Type | Activity Name | Parameter Label | Type | Options (Separated by Comma) | Display Order | UOM | Section
ACT-002 | LT Energy Meter Reading | MSB / Sub Feeder | textview |  | 1 | Status
ACT-002 | LT Energy Meter Reading | Initial Meter reading¦UOM,Final Meter reading¦UOM,Consumption | Comsumption |  | 2 | kWh
ACT-003 | HT Panel Daily Checklist | Check the cleanliness of RMU & Meter Yard, Meter panel, ATS, HT indoor and outdoor panel and clean if required.Is it free from dirst and dust. | Single Choice | Yes,No | 1 | Status
ACT-003 | HT Panel Daily Checklist | Entry door & Lock working Condition | Single Choice | Normal,Abnormal | 2 | Status
ACT-003 | HT Panel Daily Checklist | General Lighting condition | Single Choice | Normal,Abnormal | 3 | Status
ACT-003 | HT Panel Daily Checklist | Emergency Lighting condition | Single Choice | Normal,Abnormal | 4 | Status
ACT-003 | HT Panel Daily Checklist | Check for correct class of fire extinguisher provided with signages | Single Choice | Yes,No | 5 | Status
ACT-003 | HT Panel Daily Checklist | Check for proper electrical insulation/Static matt provided | Single Choice | Yes,No | 6 | Status
ACT-003 | HT Panel Daily Checklist | Check for proper dressing of all cables and proper identification | Single Choice | Yes,No | 7 | Status
ACT-003 | HT Panel Daily Checklist | Check proper electrical drawing displayed for input/output Distributions | Single Choice | Yes,No | 8 | Status
ACT-003 | HT Panel Daily Checklist | Check and ensure electrical shock treatment chart provided | Single Choice | Yes,No | 9 | Status
ACT-003 | HT Panel Daily Checklist | Check for escalation matrix displayed and DOs & DON’Ts of Electrical system | Single Choice | Yes,No | 10 | Status
ACT-003 | HT Panel Daily Checklist | Check the RMU BESCOM source which is loaded | Single Choice | Normal,Abnormal | 11 | Status
ACT-003 | HT Panel Daily Checklist | Check the PF at BESCOM meter and maintain | text |  | 12 | %
ACT-003 | HT Panel Daily Checklist | Check the Recorded MD at BESCOM meter and maintain | text |  | 13 | kVA
ACT-003 | HT Panel Daily Checklist | Check the operation of ATS during power change over | Single Choice | Normal,Abnormal | 14 | Status
ACT-003 | HT Panel Daily Checklist | Check the operation of HT indoor panel during power change over. | Single Choice | Normal,Abnormal | 15 | Status
ACT-003 | HT Panel Daily Checklist | Check all HT panel indication meters & lamps. | Single Choice | Normal,Abnormal | 16 | Status
ACT-004 | Transformer Daily Checklist | Ensure external cleanliness of transformer and clean if required | Single Choice | Ok, Not Ok | 1 | Status
ACT-004 | Transformer Daily Checklist | Check the operation of tap changer according to voltage | Single Choice | Normal,Abnormal | 2 | Status
ACT-004 | Transformer Daily Checklist | Ensure the selector switch is in auto mode. | Single Choice | Manual,Auto | 3 | Status
ACT-004 | Transformer Daily Checklist | Check for any abnormal noise from the transformer. | Single Choice | Yes,No | 4 | Status
ACT-004 | Transformer Daily Checklist | Check the working condition of transformer exhaust fan | Single Choice | Normal,Abnormal | 5 | Status
ACT-004 | Transformer Daily Checklist | Check winding Temperature | text |  | 6 | deg. C
ACT-004 | Transformer Daily Checklist | Check transformer oil level & Leakage | Single Choice | Normal,Abnormal | 7 | Status
ACT-004 | Transformer Daily Checklist | Check colour of silica jell in breather | Single Choice | Normal,Abnormal | 8 | Status
ACT-004 | Transformer Daily Checklist | Ensure transformer O/P neutral to earth voltage | text |  | 9 | Volt
ACT-004 | Transformer Daily Checklist | Check transformer surrounding lights | Single Choice | Normal,Abnormal | 10 | Status
ACT-005 | Panel Weekly PM Checklist | Inform the user Department and get the approval. Is the Approval taken for Preventive Maintenance | Single Choice | Yes,No | 1 | Status
ACT-005 | Panel Weekly PM Checklist | Ensure all breakers are at OFF position | Single Choice | Yes,No | 2 | Status
ACT-005 | Panel Weekly PM Checklist | Ensure to apply LOTO | Single Choice | LOTO Applied , LOTO not applied | 3 | Status
ACT-005 | Panel Weekly PM Checklist | Use protective personal equipment while carrying out PPM | Single Choice | Yes,No | 4 | Status
ACT-005 | Panel Weekly PM Checklist | Check for physical damage, corrosion, or signs of overheating on the panel surface. | Single Choice | Normal,Abnormal | 5 | Status
ACT-005 | Panel Weekly PM Checklist | Ensure no loose components or foreign objects inside the panel. | Single Choice | Normal,Abnormal | 6 | Status
ACT-005 | Panel Weekly PM Checklist | Verify that warning labels and indicators are clear and intact. | Single Choice | Normal,Abnormal | 7 | Status
ACT-005 | Panel Weekly PM Checklist | Clean the panel with a dry cloth or a vacuum cleaner to remove dust and debris. | Single Choice | Yes,No | 8 | Status
ACT-005 | Panel Weekly PM Checklist | Use appropriate cleaning agents for stubborn stains or grease. | Single Choice | Yes,No | 9 | Status
ACT-005 | Panel Weekly PM Checklist | Ensure the panel is powered off before cleaning to avoid electrical hazards. | Single Choice | Yes,No | 10 | Status
ACT-005 | Panel Weekly PM Checklist | Check the tightness of power cable terminations. | Single Choice | Normal,Abnormal | 11 | Status
ACT-005 | Panel Weekly PM Checklist | Inspect control cable connections for snugness and security. | Single Choice | Normal,Abnormal | 12 | Status
ACT-005 | Panel Weekly PM Checklist | Tighten any loose bolts, nuts, or connectors. | Single Choice | Yes,No | 13 | Status
ACT-005 | Panel Weekly PM Checklist | Apply grease to areas requiring lubrication for smooth operation. | Single Choice | Yes,No | 14 | Status
ACT-005 | Panel Weekly PM Checklist | Inspect and test breaker/MCCB operations for proper functionality. | Single Choice | Yes,No | 15 | Status
ACT-005 | Panel Weekly PM Checklist | Check sliding contacts physical /operational condition | Single Choice | Normal,Abnormal | 16 | Status
ACT-005 | Panel Weekly PM Checklist | Replace sliding contacts if worn out | Single Choice | Yes,No | 17 | Status
ACT-005 | Panel Weekly PM Checklist | Check indicator lamps physical/operational condition | Single Choice | Normal,Abnormal | 18 | Status
ACT-005 | Panel Weekly PM Checklist | Check indicator lamps and replace faulty ones. | Single Choice | Yes,No | 19 | Status
ACT-005 | Panel Weekly PM Checklist | Test interlocking mechanisms to ensure proper functioning. | Single Choice | Normal,Abnormal | 20 | Status
ACT-005 | Panel Weekly PM Checklist | Check bus bar connections for tightness and signs of corrosion. | Single Choice | Normal,Abnormal | 21 | Status
ACT-005 | Panel Weekly PM Checklist | Inspect lugs on their physical condition | Single Choice | Normal,Abnormal | 22 | Status
ACT-005 | Panel Weekly PM Checklist | Replace the lugs (if any) that show signs of wear or damage. | Single Choice | Yes,No | 23 | Status
ACT-005 | Panel Weekly PM Checklist | Check the panel body earthing for continuity and proper connection. | Single Choice | Normal,Abnormal | 24 | Status
ACT-005 | Panel Weekly PM Checklist | Ensure that the earthing system is intact and functioning effectively. | Single Choice | Normal,Abnormal | 25 | Status
ACT-005 | Panel Weekly PM Checklist | Removing only your own locks and tags. | Single Choice | Yes,No | 26 | Status
ACT-005 | Panel Weekly PM Checklist | Take note of the switches/breakers in the OFF position before shutdown and ensure they stay OFF when the power is turned back ON. | Single Choice | ON,OFF | 27 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Inform the user Department and get the approval | Single Choice | Yes,No | 1 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Ensure all breakers are at OFF position | Single Choice | Yes,No | 2 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Ensure to apply LOTO | Single Choice | Yes,No | 3 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Use protective personal equipment while carrying out PPM | Single Choice | Yes,No | 4 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Inspect the chiller and surrounding area for leaks, damages, or unusual noises. | Single Choice | Normal,Abnormal | 5 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Clean the condenser coils and evaporator coils to remove dirt, debris, and dust. | Single Choice | Yes,No | 6 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Monitor and maintain optimal refrigerant levels per manufacturer specifications. | Single Choice | Normal,Abnormal | 7 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Inspect for any signs of leaks in the refrigerant lines. | Single Choice | Normal,Abnormal | 8 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Inspect electrical connections, wirings, and control panels for wear, corrosion, or loose connections. | Single Choice | Normal,Abnormal | 9 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Test and calibrate control systems, sensors, and thermostats. | Single Choice | Completed, Work In Progress | 10 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Check fan blades for wear, balance, and proper alignment. | Single Choice | Normal,Abnormal | 11 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Lubricate fan motor bearings (if required) | Single Choice | Yes,No, Not Required | 12 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Inspect the compressor for any signs of oil leaks, vibrations, or abnormal noises. | Single Choice | Normal,Abnormal | 13 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Monitor compressor operating temperatures and pressures. | Single Choice | Normal,Abnormal | 14 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Inspect water piping, valves, and connections for leaks or corrosion. | Single Choice | Normal,Abnormal | 15 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Check the water treatment system for proper functioning. | Single Choice | Yes,No | 16 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Test safety controls, pressure relief valves, and emergency shutdown systems. | Single Choice | Yes,No | 17 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Ensure alarms activates correctly during faults or abnormal conditions. | Single Choice | Yes,No | 18 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Access panels or covers securely closed after completing maintenance. | Single Choice | Yes,No | 19 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Conduct performance tests to ensure the chiller operates within specified parameters. | Single Choice | Normal,Abnormal | 20 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Record operating temperatures, pressures, and power consumption. | Single Choice | Yes,No | 21 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Removing only your own locks and tags. | Single Choice | Yes,No | 22 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Ensure all worker safe and ready. | Single Choice | Yes,No | 23 | Status
ACT-006 | AC Chiller Weekly PM Checklist | Take note of the switches/breakers in the OFF position before shutdown and ensure they stay OFF when the power is turned back on. | Single Choice | ON,OFF | 24 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Inform the user Department and get the approval | Single Choice | Yes,No | 1 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Ensure all breakers are at OFF position | Single Choice | Yes,No | 2 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Ensure to apply LOTO | Single Choice | Yes,No | 3 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Use protective personal equipment while carrying out PPM | Single Choice | Yes,No | 4 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Inspect the chiller unit and the surrounding area for leaks, damages, or abnormal noises. | Single Choice | Normal,Abnormal | 5 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Clean the condenser and evaporator tubes to remove any fouling or scale buildup. | Single Choice | Yes,No | 6 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Check for any corrosion or damage on the surfaces. | Single Choice | Normal,Abnormal | 7 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Repair the damaged surfaces (if any) | Single Choice | Repaired,Not Applicable | 8 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Monitor and maintain the refrigerant levels according to manufacturer specifications. | Single Choice | Normal,Abnormal | 9 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Inspect for refrigerant leaks in the system | Single Choice | Normal,Abnormal | 10 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Inspect for refrigerant leaks in the system | Single Choice | Aressted, Not Applicable | 11 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Inspect the water piping, valves, and connections for leaks, rust, or corrosion. | Single Choice | Normal,Abnormal | 12 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Check and clean the strainers and filters in the water system. | Single Choice | Yes,No | 13 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Check and replace the strainers and filters in the water system (if required) | Single Choice | Replaced,Not Applicable | 14 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Verify the chilled water flow rate and temperature to ensure they align with set parameters. | Single Choice | Normal,Abnormal | 15 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Adjust the flow rate (if required) | Single Choice | Yes,Not Applicable | 16 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Reset the temperature settings (if required) | Single Choice | Reset done, Reset not required | 17 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Inspect the compressor and motor for any signs of wear, leaks, or abnormal noises. | Single Choice | Normal,Abnormal | 18 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Check and lubricate motor bearings as recommended. | Single Choice | Yes,No | 19 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Inspect electrical connections, control panels, and wirings for any signs of wear or loose connections. | Single Choice | Normal,Abnormal | 20 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Test and calibrate control systems, sensors, and safety switches. | Single Choice | Calibrated,Not Calibrated | 21 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Check and maintain the water treatment system to prevent scaling or corrosion in the condenser. | Single Choice | Normal,Abnormal | 22 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Test safety controls, pressure relief valves, and emergency shutdown systems. | Single Choice | Normal,Abnormal | 23 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Ensure all alarms are operational and activate during abnormal conditions. | Single Choice | Normal,Abnormal | 24 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Access panels or covers securely closed after completing maintenance. | Single Choice | Yes,No | 25 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Removing only your own locks and tags. | Single Choice | Yes,No | 26 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Ensure all worker safe and ready. | Single Choice | Yes,No | 27 | Status
ACT-007 | WC Chiller Weekly PM Checklist | Take note of the switches/breakers in the OFF position before shutdown and ensure they stay OFF when the power is turned back on. | Single Choice | ON,OFF | 28 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Inform the user Department and get the approval | Single Choice | Yes,No | 1 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Ensure all breakers are at OFF position | Single Choice | Yes,No | 2 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Ensure to apply LOTO | Single Choice | Yes,No | 3 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Use protective personal equipment while carrying out PPM | Single Choice | Yes,No | 4 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Visually inspect the tower structure, basin, fans, and associated components for any damages or wear. | Single Choice | Normal,Abnormal | 5 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Clean the basin to remove debris, algae, and sediment buildup. | Single Choice | Cleaned,Not Cleaned | 6 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Ensure the basin is free from clogs or blockages to maintain proper water flow. | Single Choice | Yes,No | 7 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Inspect fan blades, belts, and motor assemblies for wear, alignment, and tension. | Single Choice | Normal,Abnormal | 8 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Lubricate motor bearings | Single Choice | Yes,No | 9 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Check the drive system for any issues. | Single Choice | Normal,Abnormal | 10 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Inspect the fill media for any clogging or scaling | Single Choice | Normal,Abnormal | 11 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Check the distribution system to ensure even water distribution across the fill media. | Single Choice | Normal,Abnormal | 12 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Inspect and clean drift eliminators and louvers to prevent water loss. | Single Choice | Yes,No | 13 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Check water treatment systems to prevent scaling, corrosion, and biological growth. | Single Choice | Normal,Abnormal | 14 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Chemical treatment levels tested and adjusted as needed. | Single Choice | Yes,No | 15 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Inspect pipes, valves, and connections for leaks, corrosion, or damages. | Single Choice | Normal,Abnormal | 16 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Repair or replace any damaged components. | Single Choice | Yes,No, Not Applicable | 17 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Inspect electrical connections, wirings, and panels for signs of wear, corrosion, or loose connections. | Single Choice | Normal,Abnormal | 18 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Run the cooling tower and listen for abnormal noises or vibrations. | Single Choice | Normal,Abnormal | 19 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Investigate and resolve any unusual sounds or movements. | Single Choice | Yes,No, Not Applicable | 20 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Access panels or covers securely closed after completing maintenance. | Single Choice | Yes,No | 21 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Removing only your own locks and tags. | Single Choice | Yes,No | 22 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Ensure all worker safe and ready. | Single Choice | Yes,No | 23 | Status
ACT-008 | Cooling Tower Weekly PM Checklist | Take note of the switches/breakers in the OFF position before shutdown and ensure they stay OFF when the power is turned back on. | Single Choice | ON,OFF | 24 | Status
ACT-009 | Elevator Weekly PM Checklist | Inform the user Department and get the approval | Single Choice | Yes,No | 1 | Status
ACT-009 | Elevator Weekly PM Checklist | Ensure all breakers are at OFF position | Single Choice | Yes,No | 2 | Status
ACT-009 | Elevator Weekly PM Checklist | Ensure to apply LOTO | Single Choice | Yes,No | 3 | Status
ACT-009 | Elevator Weekly PM Checklist | Use protective personal equipment while carrying out PPM | Single Choice | Yes,No | 4 | Status
ACT-009 | Elevator Weekly PM Checklist | Inspect the elevator shaft, doors, and cabin for any visible signs of wear, damage, or irregularities. | Single Choice | Normal,Abnormal | 5 | Status
ACT-009 | Elevator Weekly PM Checklist | Check the condition of safety labels and emergency information. | Single Choice | Normal,Abnormal | 6 | Status
ACT-009 | Elevator Weekly PM Checklist | Inspect and test the door operation, ensuring smooth opening and closing. | Single Choice | Normal,Abnormal | 7 | Status
ACT-009 | Elevator Weekly PM Checklist | Check for any misalignment, unusual noise, or delay in door response. | Single Choice | Normal,Abnormal | 8 | Status
ACT-009 | Elevator Weekly PM Checklist | Verify the functionality of the control panel and all buttons. | Single Choice | Normal,Abnormal | 9 | Status
ACT-009 | Elevator Weekly PM Checklist | Check for any signs of wear or damage to the control panel. | Single Choice | Normal,Abnormal | 10 | Status
ACT-009 | Elevator Weekly PM Checklist | Test the emergency stop button and ensure its immediate response. | Single Choice | Normal,Abnormal | 11 | Status
ACT-009 | Elevator Weekly PM Checklist | Check the functionality of the emergency communication system. | Single Choice | Normal,Abnormal | 12 | Status
ACT-009 | Elevator Weekly PM Checklist | Inspect wiring, connections, and terminals for any signs of overheating or damage. | Single Choice | Normal,Abnormal | 13 | Status
ACT-009 | Elevator Weekly PM Checklist | Check the condition of the motor and drive system. | Single Choice | Normal,Abnormal | 14 | Status
ACT-009 | Elevator Weekly PM Checklist | Lubricate moving parts as per the manufacturers recommendations. | Single Choice | Yes,No | 15 | Status
ACT-009 | Elevator Weekly PM Checklist | Inspect the condition of the elevator cables, pulleys, and counterweights. | Single Choice | Normal,Abnormal | 16 | Status
ACT-009 | Elevator Weekly PM Checklist | Test and verify the proper functioning of safety features, including limit switches and sensors. | Single Choice | Normal,Abnormal | 17 | Status
ACT-009 | Elevator Weekly PM Checklist | Ensure that the safety brakes are operating correctly. | Single Choice | Normal,Abnormal | 18 | Status
ACT-009 | Elevator Weekly PM Checklist | Check and adjust the alignment and leveling of the elevator cabin. | Single Choice | Normal,Abnormal | 19 | Status
ACT-009 | Elevator Weekly PM Checklist | Verify that the cabin stops at each floor accurately. | Single Choice | Yes,No | 20 | Status
ACT-009 | Elevator Weekly PM Checklist | Check the operation of lights and fans in the cabin. | Single Choice | Normal,Abnormal | 21 | Status
ACT-009 | Elevator Weekly PM Checklist | Check the power supply and backup systems. | Single Choice | Normal,Abnormal | 22 | Status
ACT-009 | Elevator Weekly PM Checklist | Ensure the proper functioning of battery backup in case of power failure. | Single Choice | Normal,Abnormal | 23 | Status
ACT-009 | Elevator Weekly PM Checklist | Removing only your own locks and tags. | Single Choice | Yes,No | 24 | Status
ACT-009 | Elevator Weekly PM Checklist | Ensure all worker safe and ready. | Single Choice | Yes,No | 25 | Status
ACT-009 | Elevator Weekly PM Checklist | Take note of the switches/breakers in the OFF position before shutdown and ensure they stay OFF when the power is turned back on. | Single Choice | ON,OFF | 26 | Status
ACT-010 | Cooling Tower Daily Checklist | Check the structural / mechanical faults | Single Choice | Normal,Abnormal | 1 | Status
ACT-010 | Cooling Tower Daily Checklist | Check for stock levels in chemical containers | Single Choice | Normal,Abnormal | 2 | Status
ACT-010 | Cooling Tower Daily Checklist | Satisfactory prime in chemical dosing pipe work | Single Choice | Yes,No | 3 | Status
ACT-010 | Cooling Tower Daily Checklist | Check for signs of foulant build-up (eg, algae, sludge, debris, etc); | Single Choice | Yes,No | 4 | Status
ACT-010 | Cooling Tower Daily Checklist | Check the condition of the cooling tower shell, basin, fill, drift eliminator and water distribution system | Single Choice | Normal,Abnormal | 5 | Status
ACT-010 | Cooling Tower Daily Checklist | Check for any water leaks (eg, overflow, splash-over, excessive bleed-off); | Single Choice | Normal,Abnormal | 6 | Status
ACT-010 | Cooling Tower Daily Checklist | Check for any blockage or restricted air intake (eg, from plastic bags / rubbish) and Excessive foaming. | Single Choice | Normal,Abnormal | 7 | Status
ACT-010 | Cooling Tower Daily Checklist | Check the cooling fan Operation | Single Choice | Normal,Abnormal | 8 | Status
ACT-012 | Elevator Daily Checklist | Check if the Lift Car Call button is functional or not | Single Choice | Functional,Non-Functional | 1 | Status
ACT-012 | Elevator Daily Checklist | Check for any abnormal noise observed from the lift car door | Single Choice | Yes,No | 2 | Status
ACT-012 | Elevator Daily Checklist | Check for any abnormal noise observed from the lift car rope(s) | Single Choice | Yes,No | 3 | Status
ACT-012 | Elevator Daily Checklist | Check if the Lift Car landing Call button is functional or not | Single Choice | Functional,Non-Functional | 4 | Status
ACT-012 | Elevator Daily Checklist | Check if the emergency light in the lift car is functional | Single Choice | Functional,Non-Functional | 5 | Status
ACT-012 | Elevator Daily Checklist | Check if the emergency intercom in the lift car is functional | Single Choice | Functional,Non-Functional | 6 | Status
ACT-012 | Elevator Daily Checklist | Check if the emergency buzzer in the lift car is functional | Single Choice | Functional,Non-Functional | 7 | Status
ACT-012 | Elevator Daily Checklist | Check if the car lights are functional | Single Choice | Functional,Non-Functional | 8 | Status
ACT-012 | Elevator Daily Checklist | Check if the Automatic Rescue Device of the Lift is functional | Single Choice | Functional,Non-Functional | 9 | Status
ACT-012 | Elevator Daily Checklist | Check if the lift car is landing at the correct level of the floor | Single Choice | Normal,Abnormal | 10 | Status
ACT-012 | Elevator Daily Checklist | Check for the cleanliness of all floors and car sill of the lift | Single Choice | Yes,No | 11 | Status
ACT-012 | Elevator Daily Checklist | Check if the lift announcement system is functional | Single Choice | Functional,Non-Functional | 12 | Status
ACT-012 | Elevator Daily Checklist | Check if the Lift car doors are functioning normal | Single Choice | Normal,Abnormal | 13 | Status
ACT-012 | Elevator Daily Checklist | Check for any abnormal noise during the lift car movement | Single Choice | Yes,No | 14 | Status
ACT-012 | Elevator Daily Checklist | Check ofr any abnormal noise in lift motor | Single Choice | Yes,No | 15 | Status
ACT-012 | Elevator Daily Checklist | Check for the proper functionality of the lift car pressurization fan | Single Choice | Normal,Abnormal | 16 | Status
ACT-012 | Elevator Daily Checklist | Check for the mode of the lift car fan status | Single Choice | Manual,Auto | 17 | Status
ACT-012 | Elevator Daily Checklist | Check ofr any vibration in the lift car duing movement | Single Choice | Yes,No | 18 | Status
ACT-012 | Elevator Daily Checklist | Check for the functionality of the Lift Shaft Lighting | Single Choice | Functional,Non-Functional | 19 | Status
ACT-012 | Elevator Daily Checklist | Check for the functionality of the Lift Lobby Lighting | Single Choice | Functional,Non-Functional | 20 | Status
ACT-012 | Elevator Daily Checklist | Check for the Rescue Instructions and Escalation Matrix displayed inside and Lift Car | Single Choice | Yes,No | 21 | Status
ACT-012 | Elevator Daily Checklist | Check the functinality of the Lift Electrical Panels | Single Choice | Normal,Abnormal | 22 | Status

## Master Data
Activity Type | Service Type | Frequency | Group
JobCard | TECHSERVICES | unplanned | 1F MST
Planned | SOFTSERVICES | every1hour | 4F MST
Checklist | TRANSPORTSERVICES | every2hour | AHU Operator
Audit | SECURITYSERVICES | every3hour | Assistant Facility Manage
|  | every4hour | BCSL Security Guard
|  | every5hour | BMS Operator
|  | every6hour | Building Manager
|  | every7hour | Carpenter
|  | every8hour | Complex Manager
|  | every9hour | Customer Support
|  | every10hour | DG Operator
|  | every11hour | Digitalization Lead
|  | every12hour | Duty Manager
|  | twiceinaday | EHS Manager
Electrician
Engineer (Maintenance)
Fabricator (Welder)
Facility Team
Fire & Safety Officer
Fire Technician
Head SME
Helpdesk
HK Janitor
HK Lead (SP)
HK Supervisor
Horti Lead (SP)
Horticulture Supervisor
HVAC
HVAC Operator
HVAC Technician
Indentor
InventoryBM
InventoryFM
IT Team
Lift Operator
M&E
Maintainance
Manager
Mason
MCBS Security Guard
MEP Head
MHPL Security Guard
MIS Executive
MST
Oriole Team
Painter
Pantry Boy
Plumber
QHSE Campus Head
Security Guard
Security Lead (SP)
Security Manager
Security Officer
Security Safety officer
Security Supervisor
SITE SME
Site SME (Horticulture Se
Site SME (Soft Service)
SME
SME - Civil Infra
SME - Electrical
SME - Fire and Life Safety
SME - HVAC
SME - PHE
SME - STP and WTP
Stores
STP Operator
Technical Manager (Electri
Technical Manager (Mechani
Technical Supervisor
Technician
TQHSE Lead
Transport Desk
Unit Manager
Vittalreddy Security Guar
VP Assets