## Activity
Activity Code (Should be unique for each Activity) | Form Name | Activity Name | Activity Type | Service Type | Asset Codes (Separated by ¦ [pipe]) | Frequency | Assigned Days | Day Of Month | Quarter | HalfYear | Year | Start Date (Date the task should be scheduled from) | Start Time | End Time | Task Duration (In Minutes) | Group Name
ACT-002 | DG A Check Logsheet | DG A Check Logsheet | JobCard | TECHSERVICES | TRDB000892¦TRDB000893¦TRDB000894¦TRDB000895¦TRDB000896¦TRDB000897 | onceinaday | 2¦3¦4¦5¦6¦7 |  |  |  |  | 2025-04-09 | 00:00:00 | 23:59:59 | 1440 | Electrician

## Form Parameter
Activity Type | Activity Name | Parameter Label | Type | Options (Separated by Comma) | Display Order | UOM | Section
ACT-002 | DG A Check Logsheet | Ensure the D.G is in Manual mode while checking | Single Choice | Manual,Auto | 1 | Status
ACT-002 | DG A Check Logsheet | Check for oil Level | Single Choice | Low,Medium,High | 2 | Status
ACT-002 | DG A Check Logsheet | Check Radiator water level in DG radiator physically | Single Choice | Upto the brim,below the brim | 3 | Status
ACT-002 | DG A Check Logsheet | Check the Diesel line valves are open | Single Choice | Open,Closed | 4 | Status
ACT-002 | DG A Check Logsheet | Diesel water separator status | Single Choice | Below Red Mark, Above Red Mark | 5 | Status
ACT-002 | DG A Check Logsheet | Check & note diesel level in the Day tank | textbox |  | 6 | %
ACT-002 | DG A Check Logsheet | Check & note diesel level in the Header tank | textbox |  | 7 | %
ACT-002 | DG A Check Logsheet | Check the toggle switch in the idle mode | Single Choice | Yes,No | 8 | Status
ACT-002 | DG A Check Logsheet | Ensure the engine is clean and free from dust | Single Choice | Yes,No | 9 | Status
ACT-002 | DG A Check Logsheet | Check for any leakage | Single Choice | Yes,No | 10 | Status
ACT-002 | DG A Check Logsheet | Check air filter and indicator status | Single Choice | Normal,Abnormal | 11 | Status
ACT-002 | DG A Check Logsheet | Check the lube oil circulation pump working | Single Choice | Normal,Abnormal | 12 | Status
ACT-002 | DG A Check Logsheet | Check the ventilation of the DG Room | Single Choice | Normal,Abnormal | 13 | Status
ACT-002 | DG A Check Logsheet | Check The PLC Selector switches for the DGs, Pumps, Cooling Towers etc. In Auto Mode | Single Choice | Manual,Auto | 14 | Status
ACT-002 | DG A Check Logsheet | Battery voltage to be checked, if necessary add electrolyte (should be 15mm above the plates) | text |  | 15 | Volt
ACT-002 | DG A Check Logsheet | Check the RPM | text |  | 16 | RPM
ACT-002 | DG A Check Logsheet | Check the jacket water temperature | text |  | 17 | deg. C
ACT-002 | DG A Check Logsheet | Check the lube oil pressure | text |  | 18 | kg/cm2
ACT-002 | DG A Check Logsheet | Ensure all the display parameters are working | Single Choice | Normal,Abnormal | 19 | Status
ACT-002 | DG A Check Logsheet | Check for any alarm on the panel | Single Choice | Yes,No | 20 | Status
ACT-002 | DG A Check Logsheet | Check and record the voltage | text |  | 21 | Volt
ACT-002 | DG A Check Logsheet | Check and record the frequency | text |  | 22 | Hz
ACT-002 | DG A Check Logsheet | Check for any all temp, abnormal vibration, leakage, & noise | Single Choice | Normal,Abnormal | 23 | Status
ACT-002 | DG A Check Logsheet | Check the radiator water level indicator | text |  | 24 | %
ACT-002 | DG A Check Logsheet | Check the Air filter Indicator | Single Choice | Normal,Abnormal | 25 | Status
ACT-002 | DG A Check Logsheet | Check dynamo charging voltage (24 Volts) | text |  | 26 | Volt
ACT-002 | DG A Check Logsheet | Check the smoke condition | Single Choice | Normal,Abnormal | 27 | Status
ACT-002 | DG A Check Logsheet | Put DG selector switch is in AUTO mode post A Check is complete | Single Choice | Manual,Auto | 28 | Status

## Master Data
Activity Type | Service Type | Frequency | Group
JobCard | TECHSERVICES | unplanned | 1F MST
Planned | SOFTSERVICES | every1hour | 4F MST
Checklist | TRANSPORTSERVICES | every2hour | AHU Operator
Audit | SECURITYSERVICES | every3hour | Assistant Facility Manage
|  | every4hour | BCSL Security Guard
|  | every5hour | BMS Operator
|  | every6hour | Building Manager
|  | every7hour | Carpenter
|  | every8hour | Complex Manager
|  | every9hour | Customer Support
|  | every10hour | DG Operator
|  | every11hour | Digitalization Lead
|  | every12hour | Duty Manager
|  | twiceinaday | EHS Manager
Electrician
Engineer (Maintenance)
Fabricator (Welder)
Facility Team
Fire & Safety Officer
Fire Technician
Head SME
Helpdesk
HK Janitor
HK Lead (SP)
HK Supervisor
Horti Lead (SP)
Horticulture Supervisor
HVAC
HVAC Operator
HVAC Technician
Indentor
InventoryBM
InventoryFM
IT Team
Lift Operator
M&E
Maintainance
Manager
Mason
MCBS Security Guard
MEP Head
MHPL Security Guard
MIS Executive
MST
Oriole Team
Painter
Pantry Boy
Plumber
QHSE Campus Head
Security Guard
Security Lead (SP)
Security Manager
Security Officer
Security Safety officer
Security Supervisor
SITE SME
Site SME (Horticulture Se
Site SME (Soft Service)
SME
SME - Civil Infra
SME - Electrical
SME - Fire and Life Safety
SME - HVAC
SME - PHE
SME - STP and WTP
Stores
STP Operator
Technical Manager (Electri
Technical Manager (Mechani
Technical Supervisor
Technician
TQHSE Lead
Transport Desk
Unit Manager
Vittalreddy Security Guar
VP Assets